To start this small version of HYDROFLO 1.2 ...

- print this document file

- insert the diskette in drive A:

- move to that diskette drive by typing " A: " then press RETURN

- type " DEMO " and press RETURN.

HYDROFLO will then load.

A letter to interested parties...

" CAUTION " U.K. users should note that reference to " English Units ",

using the terms Gallons and GPM etc. MEANS U.S. Gallons and the

necessary conversions should be allowed for.

Dear Engineer,

On this disk or residing in this directory is a small version of

Engineering Software's HYDROFLO 1.2 along with instructions and 2

example problems.  HYDROFLO performs the functions of a linear

hydraulic design tool for systems conveying fluids from point to

point.  It runs on the IBM PC and the related family of PC/MS-DOS

microcomputers.  We are excited about this software because there

are no comparable packages on the market today in terms of its

capabilities and price.

The design engineer essentially works in a worksheet type

environment, analyzing hydraulic elements and observing the bottom

line effects.  HYDROFLO's extensive flexibility starts with the fact

that calculations can be performed in English or metric units and

use any type of fluid.  All of Engineering Software's packages have

this basic capability.  The full featured version includes the

UTILITY functions where with a single command the entire system's

diameter or friction can be changed to a new value and the system's

new operating point and pump specification be determined.

The engineer can specify that a pump be prescribed for a system

to meet a specified flow.  Cavitation calculations are made and

reports detailing the system's head losses for various flows are

provided.  This demo is a working version in that your own hydraulic

calculations can be performed and verified.  It is a good way to

evaluate HYDROFLO risk free.  Full screen graphics of the system

and pump operation are accessible along with the full functions

in the REPORT option.

The full featured version costs 250 Pounds Sterling, and includes

a User's Guide with numerous examples and a hydraulic reference handbook.

Tele-phone support is available at no cost to registered users.

ORDER FORM

Name: ________________________________  Title: ____________________

Firm: ________________________________  Phone: ____________________

Address: __________________________________________________________

__________________________________________________________

__________________________________________________________

Post Code: ____________________

Both 5 1/4" and 3 1/2" diskettes are included in all packages.  Prices

subject to change.

U.K. PRICE LIST ------  APRIL 1991

Quantity      Product                                                                                              Total

____________  HYDRONET 3.0  (550 Pounds Sterling each)      _________

____________  HYDROFLO 1.2  (250   " "    "  "   each)      _________

____________  H-CALC 1.0    (120   " "    "  "   each)      _________

THE BUMPER BUNDLE PACKAGE :

____________  All Three     (750 Pounds Sterling - Total)  _________

ADD V.A.T. @ 17.5 %                           _________

Total Enclosed _________

Check  or  M.O.  enclosed _____

Make checks payable and mail to:

PISCES ENGINEERING SERVICES

12 LOCH LAXFORD,

ST. LEONARDS,

EAST KILBRIDE  G74 2DL

PHONE & FAX (03552) 43220

This is an abbreviated form of the HYDROFLO 1.2 manual...

INTRODUCTION

HYDROFLO is a tool for use in the design and validation of hydraulic systems.

It solves four common type of problems...

1) with a known pump, find the operating point of the system,

2) prescribe a pump for a system to drive a desired flow,

3) find the steady-state gravity flow for a pipeline, and

4) find element and total head losses for a non-pump system.

Pipe head losses in hydraulic systems can be calculated using the

Hazen-Williams equation for water or using the Darcy-Wiesbach equation for

any fluid.  All system calculations can be performed in either English or

metric units.  Two choices for head and flow units are available within each

unit system.

The user describes a hydraulic system consisting of inlets, outlets, valves,

fittings, pumps and pipes.  If a pump is to be included in the system, the

user has the option of defining the pump curve or letting HYDROFLO prescribe

one for the system.  Net positive suction head (NPSH) calculations for

cavitation determination and pump specification are provided.  A menu of

valves and fittings is provided for selection.  Given the fitting diameter,

the corresponding friction value is automatically used by HYDROFLO in the

head loss calculations.  Custom friction values may also be entered.  Default

system configurations of data file directories, fluid properties, head loss

equations, pressures and units systems can be set for automatic use at system

start-up.

Besides the basic ability to edit single element data, a large scale system

editing feature allows all system element diameters and friction values to be

changed with one command.  A system analyzer is also available to scrutinized

data for incompleteness or inaccuracies. Output reports summarize suction,

discharge and total system head losses and detail individual element

velocities and head losses.  A graph of the pump and system operating curves

is constructed for various flows and can be output to the screen and printer.

The current system data can be saved at any point of design in compact data

files.

UNDERLYING  THEORIES

PIPES

Two head loss equations are available for determining the major friction

losses in pipes.  The question of which equation to use depends on the system

fluid type and conditions.  Certain conditions exist where either equation may

be used and comparing the results of both will confirm the proper modeling of

system operation.

The Hazen-Williams equation is available for water systems under turbulent

flow conditions and at 60 degrees F. (or fluids with kinematic viscosity

around 1.2x10-5 ft2/s).  To use this equation, Hazen-Williams coefficients are

needed for all pipes.  These coefficients have been determined by empirical

methods.

The fundamentally based Darcy-Wiesbach equation can be used for fluids of

various viscosities.  The kinematic viscosity of the fluid in use must be

known as well as the piping material's specific roughness (sometimes called

absolute roughness).  HYDROFLO uses a Colebrook-White algorithm to determine

the Moody friction factor f so manual look-up of values on the Moody diagram

is not needed.

FITTINGS  AND  VALVES

Minor friction losses through fittings and valves (which includes inlets and

exits) in water systems are modeled by multiplying the velocity head by the

appropriate resistance coefficient, K.  HYDROFLO automatically uses the proper

values upon menu selection of the type and diameter.  Custom K values may also

be input for fittings and valves not listed.  It is important to check the

operating flow velocity to ensure the complete opening and therefore the

correct friction factor for the fitting.

Friction loss data for fittings and valves in fluid systems other than water

are not in reliable supply.  The best approach is to assume turbulent flow

conditions and use the equivalent length method.  The fittings can then be

represented as pipe elements in HYDROFLO.

Pressurized tanks at the inlet and exit may be modeled by inputing different

absolute pressures other than atmospheric at those points.  Standard

atmospheric pressures at the inlet and exit would be used for open air intake

and discharges (see tables in APPENDIX).  The inlet and exit pressure

difference is converted to equivalent feet (or meters) of liquid and is then

added to the elevation difference to obtain the total system static head.

SYSTEM CURVES

Two system curves are drawn on the graphs displayed in the REPORT - GRAPH

option of HYDROFLO.  The two upward increasing curves are the combination of

all valve losses plus 90 and 110% of the pipe losses at the user specified

friction values.  This provides a sensitivity analysis.  The further the two

curves are apart, the more sensitive the system is to variations in pipe

friction coefficients.  The other downward decreasing curve defines pump

operation. The hydraulic system will operate at the intersection of the system

and pump curves.

NPSHA

The Net Positive Suction Head Available (NPSHA) calculation is critical for

assessing cavitation possibilities in a hydraulic design using pumps.  It is

the total suction head in feet (or meters) of liquid (absolute at the pump

centerline or impeller eye) less the absolute vapor pressure in feet (or

meters) of the liquid being pumped.  If this calculation is of low or negative

value, you can be assured that the hydraulic design is near non-functional.

The situation can be remedied by placing the pump closer to the inlet or in

some way increase the suction dynamic head (or reduce the suction static lift).

PUMPS

A pump need not be incorporated into a design using HYDROFLO.  The user can

merely be analyzing the head losses on a line composed of pipes and fittings.

HYDROFLO provides two ways to include pumps in your hydraulic design.  You

may let HYDROFLO prescribe a pump that will supply the design flow for the

system or you may define a pump by inputing four points from the pump curve

and let HYDROFLO determine the actual operating point of the system.

Setting the DESIGN (ANALYSIS) FLOW amount in the STATUS option to a desired

value and requesting that a pump be prescribed when in DEFINE, forces HYDROFLO

to plot the curve of a pump that will supply the desired flow. The curve

presented is a ideal representation for a pump that has its optimal operating

point at the intersection of the system curve at the design flow.

Realistically, there may be no such pump in existence.  But this gives the

engineer a starting point in the search for the required pump.  Once a close

fit is found the actual pump curve may be entered and the actual operating

point may be determined.  Throttle valves may then be used to to bring the

pump to the desired operating point.

If the user chooses to define a pump for the system, four points off the curve

are needed as input.  HYDROFLO will fit these points to a cubic equation and

have a continuous function for the determination of pump head values.

START-UP

To start HYDROFLO, move to the disk drive that contains the HYDROFLO diskette

(ie, type A: or B: and press RETURN) then from that drive, type DEMO at the

DOS prompt and press RETURN.

HYDROFLO will take a few seconds to load.  The first screen lists the features

in the full-feature version and where you can obtain it.  Press any key to

start this small version of HYDROFLO.  The top line of the main HYDROFLO

screen displays the HYDROFLO copyright notice on the left and the current

system filename on the right.  The bottom line of the screen has the computer

time and date on the left and the right has an error space reserved for when

errors occur during system operation.  The various keystrokes available as

responses for any HYDROFLO prompt is displayed on the line above the bottom

line of the screen.

HYDROFLO uses the following Lotus-style menus and keystroke syntax.

To select an option from a displayed menu:

- Use the space bar or cursor arrows to hi-light the option and press RETURN.

- or press the first character of the option name.

To exit from a lower menu or operation:

- Press the escape key (Esc).  (Note:  pressing escape repeatedly will

eventually bring you back to the main menu but never let you fully

exit to DOS. You must press "Y" at QUIT).

A help facility is available by pressing the F1 (function) key anywhere during

program execution.

When entering characters or numbers a toggle between insert mode and overtype

mode is available by pressing the insert (Ins) key.

MENU OPTIONS

FILE

The FILE option allows the retrieval from and storage to disk of data files.

The HYDROFLO data file names are appended with the extension of .FLO

automatically, the user need not type it in.

Select the RETRIEVE sub-option and a screen of data filenames will be

displayed.  Use the space bar or cursor arrows to hi-light the desired

filename and press RETURN to retrieve the data in the file.  The user may also

press function key F2 and input a custom path and filename.  The data will

load and the main screen will return and the current filename will be

displayed in the upper right corner.  The data is now available for use.

When SAVE is selected, the current path and filename are displayed if a system

has been loaded.  Pressing RETURN retains the original filename and the user

is prompted with a warning:

file exists!   Cancel  Replace

Press "R" to overwrite the data file or "C" (or Esc) to cancel the operation.

Pressing escape (Esc) at the current path and filename presents the just the

current path ready for the user to enter a new filename.  Pressing escape

again allows a totally new path and filename to be entered.

To clear the current data from HYDROFLO's memory (not erase the disk datafile)

without exiting the program, see the later section on utilities for editing.

STATUS

The STATUS option is used to set the default data file directory, head loss

equation, units systems, fluid properties, default friction coefficients and

pressures.  The cursor arrows up or down (down arrow same as RETURN) are used

to move between the various input fields.  Pressing the escape key (or coming

to the end of the menu) leads to the prompt:

Reset current system to new values?     NO     YES

If the new values aren't correct, press the escape key (Esc) or "N" to return

to the main menu.  If they are correct, press RETURN and the system will use

the new parameter values and the following prompt will appear:

Update default parameter file?     NO     YES

This prompt will only appear if the previous prompt is answered with  "Y" .

A  "Y"  response to this question will update the HYDROFLO default value file

that is loaded on start-up.  The values displayed will be automatically set.

This is a time saver in establishing new designs.  For example, if an engineer

always uses the Darcy-Wiesbach equation and analyzes oil conveyance systems,

HYDROFLO will start with these parameters automatically.  On hard disk systems,

each person can have their own user directory and HYDROFLO configuration with

the desired parameters viewing only their data files while using a central

directory for the HYDROFLO system files.

PARAMETER DESCRIPTIONS

The DATA FILE DIRECTORY is the path where HYDROFLO looks for data files (shown

in the FILE - RETRIEVE option).  HYDROFLO assures that the directory entered

exists before the user can move on to selecting which head loss equation to

use.  On a hard disk system, this DATA FILE DIRECTORY should be set to the

user's own sub-directory.

Pressing RETURN or the cursor down arrow hi-lights the HEAD CALCULATION

EQUATION field.  The user chooses either the Hazen-Williams or the

Darcy-Wiesbach equation by pressing arrow left or right then RETURN to select.

Press RETURN to select the head loss equation and hi-light the UNIT SYSTEM

field.  The UNIT SYSTEM and FLOW UNITS are chosen as above by pressing arrow

right or left then pressing RETURN or arrow down to select.

The DESIGN (ANALYSIS) FLOW is the flow amount desired in the design. Press

"?" (question mark) to let HYDROFLO determine the operating flow in a gravity

or pumping system with known curve.  The ANALYZE option will tell you if a

system is being interpreted correctly.

HEAD UNITS are selected like flow units above.  if using units of psi or

Kpascals, be sure to set the proper liquid specific gravity.

The DEFAULT SPECIFIC ROUGHNESS or DEFAULT H-W COEFFICIENT can be set so that

the user has to only press RETURN when performing pipe data input. This does

not change any currently defined pipe friction coefficients.  To change ALL

EXISTING pipe roughnesses to a new value, use the UTILITY - FRICTION option.

To change a specific existing pipe's roughness coefficient use the DEFINE

option and press F2 when positioned at the pipe.

The SPECIFIC GRAVITY value is needed for the conversion to head units other

than feet or meters of liquid.

The VAPOR PRESSURE is of the liquid at pumping temperature and is required for

the NPSHA (Net Positive Suction Head Available) calculation.  If there is no

pump, this can be disregarded.

ATMOSPHERIC PRESSURE AT PUMP sets the pumps external pressure and the initial

values for the pressure at the inlet and exit.  The initial default value is

for open tank sea level conditions (see tables in APPENDIX).

The KINEMATIC VISCOSITY is required when using the Darcy-Wiesbach equation.

The bottom of the STATUS screen displays your current hardware configuration.

DEFINE

The DEFINE option on the main menu allows you to ENTER and EDIT new system

elements.  This section details the type of elements available for defining.

Once elements are defined, the user can EDIT, DELETE and INSERT elements as

described in the following EDIT section.

ELEMENTS AVAILABLE FOR DEFINING ...

INLETS

The first element in a design is an inlet.  The user can select the type of

inlet from the inlet menu or press F2 and input custom values for inlet

description and resistance coefficient K.  In both cases, the inlet elevation,

diameter and pressure are asked for.  A non-zero diameter is needed to set up

the default system diameter.  The pressure value is the absolute atmospheric

pressure at the surface of liquid supply level (barometric pressure from an

open tank or absolute pressure existing in a closed tank).  This value of

pressure is needed for the NPSHA calculation.  If using HYDROFLO to obtain

simple head loss values for other element than inlets, a zero value of K for

the inlet will omit inlet losses from REPORT option totals.

PIPES

The data entered for pipes include  description, diameter, length and friction

factor.  The optional descriptions for all elements are for the use of the

user for identification purposes.  The friction factor that appears will be

either the default specific roughness or the default H-W coefficient and is

available for editing.  The user is free to press RETURN and use this value

or input another friction value.

VALVES & FITTINGS

The fitting menu lists numerous types of valves and fittings.  Use the cursor

arrow keys to hi-light the desired fitting and press return to select it.  The

user will then be prompted for the fitting diameter and HYDROFLO will use the

appropriate K value for the fitting in its head loss calculations.  The user

has the option of pressing F2 on the fitting menu and then inputing custom

descriptions and K values.  NOTE: when custom values are input and when then

the  UTILITY - DIAMETER  option is used, HYDROFLO will not be able to update

the fitting's K value accordingly and the user must remember to update the

value.

PUMPS

The user has the choice of defining a pump curve for analysis or letting

HYDROFLO prescribe one for the system.  If a curve is defined, the user must

describe four equal distant points off the curve as follows.  The flow

increment sets the distance between the four points and is in units of flow.

The four points of head begin first with the shutoff head (The head at which

no flow can be push through the pump).  The remaining three points from the

curve are the head values at the flow increment, twice the flow increment and

three times the flow increment.  Once a pump is defined, the user can position

the element pointer at the pump and press F5 to obtain a plot of the pump

curve.  The pump elevation is needed for the NPSHA calculation and the

suction side calculations.  The atmospheric pressure, needed for NPSHA,

suction and discharge calculations when pressure tanks are used, is input in

the  STATUS  option.

EXITS

The last element in a hydraulic system is an exit.  The K value for exits is

normally 1.0 but the user has the option of inputing any value. The pressure

at the exit will default to the pump's atmospheric pressure.  If the discharge

is to be at a substantially different elevation or a closed tank, be sure to

update this value to the correct absolute pressure.

EDITING ...

The following keys can be used on defined elements within the DEFINE option.

EDIT (F2)

Use the cursor arrow keys to move the position pointer to an element and press

F2 (Function key 2).  The original input screen is shown with the present

values.  The user is allowed to edit or re-enter element data by inserting or

overtyping text or numeric characters.  Pressing RETURN or pressing arrow down

at a data position retains the original values shown. Pressing escape jumps

out of the editing of the current element and progresses to the next element.

DELETE (F3)

When pointing at a defined element, pressing the F3 key prompts the user for

deletion of the element.  The user confirms the request and the element is

removed.  Pressing "N" or Esc retains the element.

INSERT (F4)

When pointing at a defined element, pressing the F4 key prompts the user for

inserting an element before that element.  Again the user can confirm the

request and select the type of element to insert.  Pressing "N" or Esc aborts

the operation.

PLOT (F5)

When positioned at a pump that is not to be prescribed by HYDROFLO, the curve

for the pump is plotted on capable displays.  Pressing F6 while the plot is

shown sends the graphics display to the graphics printer.  Pressing any other

key returns to the defined element screen pages.

PG-UP  and  PG-DN

These keys allow fast movement within the pages of defined elements.

REPORT

The REPORT option allows the output of system element data, summaries of head

loss results and system curve plots.  All output can be directed to the

SCREEN, FILE or PRINTER.

The SUMMARY sub-option displays the current systems fluid properties, NPSHA

calculation, static head data, system head loss totals and pump prescription.

The DETAIL sub-option gives a listing of all elements with their friction,

diameters, velocities and head losses for a given flow.  Pipe details include

lengths.  Inlet, exit and pump details include elevations and absolute

pressures.

The GRAPH sub-option displays the system plot with pump curve and operating

point.  Pressing F6 sends the displayed graph to the printer. Pressing Esc

(escape key) while the printer receives information aborts the printing

operation.

UTILITIES

The DIAMETER sub-option allows the mass editing of ALL element diameters.

For fittings that were selected from the fitting menu, the corresponding K

value for the new diameter will be set also.  Custom fittings will have their

diameters changed so that velocities will be correct but the K values may not

be correct and must be checked and updated by the user.

The FRICTION sub-option changes ALL pipe friction values to a new value.

The ERASE sub-option clears HYDROFLO's memory of the currently defined system.

You are starting over.  NOTE: Be sure all wanted work is saved to disk with

the  FILE - SAVE  option before using ERASE.

ANALYZE

ANALYZE is a powerful option that can spot potential problems in your design.

The first few lines of output state HYDROFLO's interpretation of your problem

(whether a pump, gravity or forced flow problem) and the action to be taken

(operating point to be determined, head losses found, etc.).  In general if

HYDROFLO is unable to plot a system graph or outputs strange results, ANALYZE

may pick up the problems cause.  The warnings that this option provides are

strictly informational.  If HYDROFLO is being used to obtain simple head loss

calculations for a few elements, the warning that there is no exit or pump in

the system, is informational and of no concern.  However, if HYDROFLO is being

used to analyze an hydraulic system complete with pump, any warning message

that this option provides may be critical.  ANALYZE should be run often so

that it's warnings can be interpreted correctly from experience.

QUIT

This option is used to exit HYDROFLO.  Be sure that any altered work since the

last save is not needed.  The user will be prompted as to whether they really

wish to leave HYDROFLO and exit to the operating system.  Pressing  "N"

returns the user to the main menu.

DESIGN METHODS

A general design methodology for using HYDROFLO follows:

1.)  Enter the STATUS option and set the head loss equation, units, fluid

parameters, design flow and pressures (if these conditions are going to be

used for most new designs, you may wish to place them in the default parameter

file for automatic start-up).

2.)  Enter the DEFINE option and enter all element data starting with the

inlet.

3.)  When all data is entered, use the  FILE - SAVE  option to save the

current data.  Perform file saves often so that work is not lost.

4.)  Run the ANALYZE option to identify any incomplete or inaccurate data.

5.)  Use the REPORT option to obtain a summary of system head losses,

detailed reports of all element data and a graph of the system and pump curves.

6.)  Use the UTILITY options to investigate the effects on pump

specification that differing diameters and materials (friction) have.

DESIGN TIPS...

- If a pump is to be prescribed for the system, the design flow is the desired

flow for the system.

- When a pump is restricted to being positioned at a certain location and the

NPSHA is low, the diameters of the suction side lines can be increased to

minimize these intake losses.

- When a pump is not restricted to a specific location, the insert element

function (F4) and delete element function (F3) can be used to move the pump to

various spots in the line to provide adequate NPSHA.

- Trade offs existing between system element diameters (pipe and fitting

costs) and pump size (pump costs) can tested by using the  UTILITY - DIAMETER

option and letting HYDROFLO prescribe the pump.  The optimal solution would

be find the minimum total cost for the system while meeting the design flow

and providing an adequate NPSHA.

USING FLUIDS OTHER THAN WATER

HYDROFLO allows the analysis of hydraulic systems using fluids other than

water.  If a fluid has a kinematic viscosity near that of water at 60 degrees

F and is used at turbulent conditions, then the Hazen-Williams equation can be

used.  If those conditions are not met, the Darcy-Wiesbach equation should be

used.  The kinematic viscosity and the piping materials specific roughness

must be known.  For valve and fitting friction head losses, the best approach

is to assume turbulent flow conditions and use the equivalent length method.

The friction coefficients automatically used from the fitting and valve menu

are strictly for water.

SAMPLE PROBLEMS

DEMO PROBLEM 1

An engineer is to provide the pump curve and system pipe size needed for

the hydraulic system shown opposite.  A flow of 250 gpm is desired.  The

Hazen-Williams equation will be used to compute pipe head losses in this water

system.

The file DEMO1.FLO on the demo disk contains the data for this problem and

can be retrieved using the  FILE - RETRIEVE  option.  The following text

describes the step by step procedure for creating this file.

First, enter HYDROFLO's  STATUS  option by pressing "S" at the opening

screen or press the space bar once to move to and hi-light the  "STATUS"

phrase, then press the RETURN (ENTER) key.  Once in the STATUS option, press

the arrow down key to move past the DATA FILE DIRECTORY field to the HEAD

CALCULATION EQUATION field.  If  "Hazen-Williams"  is not displayed, press the

arrow right or left key to switch from the displayed  "Darcy-Wiesbach"

statement and press the arrow down key to move to the UNIT SYSTEM field.  It

should say  "English"  and if not, pressing arrow left or right will switch

to the desired unit system.  FLOW UNITS are selected as the above parameters

were, and we use  "gpm"  not  "cfs" .  The DESIGN (ANALYSIS) FLOW is a string

input field and so type in "250." and press the arrow down (or RETURN) key.

If any parameter field is not correct, press the arrow up key until arriving

at the desired field, then edit it accordingly.  For HEAD UNITS we want "feet

of liquid"  not  "psi"  and it is selected as FLOW UNITS was above.  Type in

"100."  and press RETURN for the DEFAULT H-W COEFFICIENT.  This system uses

water and to set the SPECIFIC GRAVITY at 1.0, just press RETURN.  The VAPOR

PRESSURE of water at 60 degrees F is ".25" psia so that value is entered and

RETURN is pressed.  Enter "14.2" for the atmospheric pressure at the pump and

press RETURN.  The following prompt will now appear...

Update current system to new values:   NO   YES

If the values set are correct, press RETURN or " Y " to accept the new

values.  If they aren't, we could press RETURN anyway to accept the values,

and then go back to the STATUS option again to edit desired fields.  If we

chose not to accept the new values at all, we could press "N" or Esc to abort

the process.  When the values are correct and are accepted, a prompt to update

the default parameter file appears.  If we wanted to use the new values each

time HYDROFLO was started, we would answer with a "Y", but for these

demonstration purposes we instead press RETURN.

Discharge elev  =  1080.63'

Supply elev  =  1012.51'

PRESSURES:

pump elev = 1005.74'

press. at pump = 14.2 psia

PIPES:

Steel sched-40 4"(est)

H-W coef = 100

(page 3-8 Cameron)

Spec Rough = .00015

(page 3-5 Cameron)

FLUID:

Water at 60 deg. F.

Vap. press. = .25 psia

(Page 4-20 Cameron)

Kin. vis  = .00001216 ft2/sec

(pg 4-4 & 4-25 Cameron)

DETAILED REPORT - INDIVIDUAL ELEMENTS

(System: DEMO1.FLO) @ flow = 250.00 gpm

El# Description                            Fric    Dia     Vel      HL

(inches) (ft/s) (feet)

1 Inlet Flush - sharp edged               0.50   4.00   6.38    0.32

Elev = 1012.51 feet   Press = 14.20 psia

2 Pipe                       l=  50.00  100.00   4.00   6.38    3.35

3 Fitt  Std. elbow-long radius 90 deg.    0.27   4.00   6.38    0.17

4 Pipe                       l=  25.00  100.00   4.00   6.38    1.67

5 Fitt  Stop check valves                 6.80   4.00   6.38    4.31

6 Fitt  Plug valve Straightway            0.31   4.00   6.38    0.20

7 Pipe                       l=   6.00  100.00   4.00   6.38    0.40

8 Pump  pump prescribed for system

Elev = 1005.74 feet   Press = 14.20 psia

9 Pipe                       l=   6.00  100.00   4.00   6.38    0.40

10 Fitt  Butterfly valve                   0.77   4.00   6.38    0.49

11 Pipe                       l=  50.00  100.00   4.00   6.38    3.35

12 Fitt  Std. elbow-long radius 90 deg.    0.27   4.00   6.38    0.17

13 Pipe                       l= 500.00  100.00   4.00   6.38   33.48

14 Fitt  Stop check valves                 6.80   4.00   6.38    4.31

15 Pipe                       l=1000.00  100.00   4.00   6.38   66.97

16 Exit                                    1.00   4.00   6.38    0.63

Elev = 1080.63 feet   Press = 14.20 psia

Back at the main HYDROFLO menu, we select the  DEFINE  option to perform

data input of the elements shown on the opposite of this side of the page.

Starting with the inlet (the element data is listed in output report opposite

side of paper).  When  DEFINE  is selected, the Inlet menu appears and the

description  "Flush - sharp edged"  is hi-lighted by pressing arrow down once,

then pressing RETURN to select.  A smaller sub-window appears that displays

the inlet description and resistance value K, and the cursor is positioned at

the elevation field.  An elevation of "1012.51" is input and the user presses

RETURN.  Our initial estimate of system diameter is 4" and that value is

entered thus setting up the default diameter for the rest of the system.  The

pressure at the inlet is the next input and since this is an open surface

intake, press RETURN to use the default atmospheric pressure (set up for the

pump in the  STATUS  option).

The element menu is automatically displayed after the inlet data input and

the position pointer is set to element #2.  Element #2 is a pipe so RETURN is

pressed and an optional description can be entered.  The next field displays

the default diameter set up for the inlet and RETURN can be pressed to accept

the value.  A length of  "50."  feet is entered for the pipe and the RETURN

key is pressed.  The default Hazen-Williams coefficient appears and the RETURN

key is again pressed to accept the value.

The element menu is displayed and the pointer is positioned at element #3.

This element is a fitting and the word "Fitt" is hi-lighted by pressing the

arrow down key and the RETURN key is pressed to select it and the fitting and

valve menu appears.  Again using the cursor arrow keys, the statement  "Std.

elbow long radius 90 deg"  is hi-lighted and the RETURN key is pressed.  The

default diameter is displayed and RETURN is pressed to accept the default

value.  HYDROFLO automatically uses the correct resistance coefficient K, for

inlets, exits, valves and fittings selected from it's internal menus.

The data for elements #4 through #7 are input in the same manner as the

previous elements.

When pump position #8 is reached, the phrase  " pump "  is hi-lighted on

the element menu and the RETURN key is pressed.  The pump window appears and

offers the choice of  "define a pump for analysis"  or  "let HYDROFLO

prescribe a pump"  for the system.  In this problem, a pump is to be

prescribed so press the arrow down key and then press RETURN.  The pump

elevation field is displayed and the value  "1005.74"  is entered an RETURN

is pressed.

The data for elements #9 through #15 is entered (according to data listed

on opposite side, detailed report) up to exit element #16.

At exit element #16, the phrase  " exit "  is hi-lighted on the element

menu and the RETURN key is pressed.  A window is displayed with the exit's

data and the cursor is positioned at the description field.  The description

is optional.  The next input field is the resistance coefficient, K.  For most

exits a value of 1.0 is used but the value may be edited.  In the elevation

field a value of  "1080.63" is entered the RETURN key is pressed.  We press

RETURN again to accept the default diameter value and again to accept the

default pressure since this is an open surface exit.

The  "defined"  mode is entered where by pressing the arrow left or right

(or page-up, page-dn) key can position the pointer at an element and display

it's data.  We can edit an individual element's data by positioning the

pointer at the element and pressing F2, insert an element by pressing F4 or

delete an element by pressing F3.

With the full featured version we could now select  FILE , then  SAVE and

specify a filename for our data to reside in.  At the main menu run the

ANALYZE  option to determine if any potential problems exist in the system.

From the main menu, the  REPORT  option can be used to preview results of

the analysis.  The operating point is determined to be at 250 gpm and 188

feet head with a NPSHA (Net Positive Suction Head Available) of 28.5 feet and

a general system velocity of 6.38 ft/sec.  Other system diameters can be

tested with the full featured of HYDROFLO using the  UTILITY - DIAMETER

option but 4" appears to be the best.  With the demo disk, the DEFINE  option

is used to edit individual element diameters using the F2 key.

The graph obtained with the  REPORT - GRAPH  option (CAPACITY vs. HEAD

graph, following) and the NPSHA value (end of SUMMARY OF PUMPING SYSTEM DATA)

would be taken to a pump manufacturer to find an appropriate pump.  Once a

close operating pump is found, it's curve is input to the system by

positioning the DEFINE pointer to the pump position and pressing F2, selecting

"define a pump"  (the top line option) then inputing it's data according to

the previously discussed DEFINE - PUMPS section and the actual operating point

will be found.

SUMMARY OF PUMPING SYSTEM DATA  (System: DEMO1.FLO)

CONFIGURATION:   Hazen-Williams Eq.

Flow                =     250.00 gpm

FLUID PROPERTIES:

Specific Gravity    =      1.000

Vapor Pressure      =       0.25 psia

STATIC HEADS:

Suction Elev Head   =       6.77 feet

Discharge Elev Head =      74.89 feet

Exit - inlet press. =       0.00 feet

Total Static Head   =      68.12 feet

NPSHA CALCULATION:

Supply pressure     =      14.20 psia (abs)

Vapor pressure      =       0.25 psia (abs)

Suction static head =       6.77 feet

Suction dynamic hd  =      10.41 feet @ design flow

NPSHA               =      28.58 feet

HEAD LOSSES (in feet)

FLOW (gpm)

SUCTION SIDE                125         250         375

MINOR LOSSES:

Valves & fittings                    1.25        4.99       11.23

MAJOR LOSSES:

Pipe HL using Hazen-Williams Eq      1.50        5.42       11.48

STATIC SUCTION HEAD:

Inlet - pump elev + pressures        6.77        6.77        6.77

TOTAL SUCTION HEAD:

Head (+), lift (-)                   4.02       -3.64      -15.94

DISCHARGE SIDE

MINOR LOSSES:

Valves & fittings                    1.40        5.60       12.59

MAJOR LOSSES:

Pipe HL using Hazen-Williams        28.90      104.20      220.61

STATIC DISCHARGE HEAD:

Exit - pump elev + pressures        74.89       74.89       74.89

TOTAL DISCHARGE HEAD:

Static head plus friction losses   105.19      184.69      308.10

TOTAL SYSTEM LOSSES

TOTAL SUCTION HEAD:

Static head + friction losses        4.02       -3.64      -15.94

TOTAL DISCHARGE HEAD:

Static head + friction losses      105.19      184.69      308.10

TOTAL SYSTEM HEAD:

Suction and discharge heads        101.18      188.33      324.04

Pump Prescription:

Design operating point:  FLOW =      250.00 gpm

HEAD =      188.33 feet

NPSHA =      28.58 feet

DEMO PROBLEM 2

A pump is to be specified for the oil conveyance system displayed opposite.

A flow of .4 m3/sec is to be delivered by the 30 cm. diameter system.  The

Darcy-Wiesbach equation will be used to calculate pipe head losses and the

valves will be modeled as pipes using the equivalent length method.  The file

DEMO2.FLO on the demo disk contains the data for this problem and can be

retrieved using the FILE - RETRIEVE option.

Using HYDROFLO's  STATUS  option, we set the Darcy-Wiesbach equation for

use in calculating pipe head losses.  The DESIGN (ANALYSIS) FLOW will be set

at .4 m3/sec.  Within the metric unit system we setup flow units of m3/sec

and head units of meters of liquid.  We will also set a default specific

roughness of .03 mm for the steel pipe.  Specific gravity and kinematic

viscosity are set to the values listed opposite.

Using the  DEFINE  option, we give the inlet a K value of 0.0 because all

fittings (except the pump) are being modeled as equivalent lengths of pipe.

On the inlet data input, press arrow up when at the elevation field and enter

"0.0" for the friction K value.  All the other data for the inlet is needed so

that static head and NPSHA calculations are performed correctly.  Using the

chart on page 3-121 in Cameron (included with full featured version) we line

up the diameter 11.8 inches (30 cm.) and the point for an ordinary entrance

and we get 17 feet of pipe length which works out to 5.18 meters.  Pipe element #2 has a length of 30 meters so we

have added this length to it.  The same process is used for the exit and its

equivalent length is add to pipe #24 and a K value of 0.0 is given to the exit.

The rest of the data is entered (pipes entered normally and valves as

pipes) along with the pump which we request to be prescribed.

The  ANALYZE  option will tell us that the inlet and exit have zero for

coefficients.  This is as intended.  The losses for the inlet and exit are

included in the adjacent pipes length.

The prescribed pump's and system's curve along with the system summary of

head losses is shown on the back of this page.

Tank B elev  =  178.15 m

Tank A elev  =  132.63 m

Pump elev = 125.79 m

PIPING SYSTEM:

Steel sched-40  30 cm.

Specific Rough = .03 mm

PRESSURES:

Atm press @ pump = 99.285 Kpa

Tank A = 121.39 Kpa (closed)

Tank B = 103.54 Kpa (closed)

FLUID:

SG = .86 Crude oil at 120 deg. F.

Kinematic Vis = 4.1 centistokes = 4.1e-6 m2/sec

Vap. press. = .5 KPa

DETAILED REPORT - INDIVIDUAL ELEMENTS

(System: DEMO2.FLO) @ flow = 0.40   m3/sec

El# Description                            Fric    Dia     Vel      HL

(cm.) (mtr/s) (meters)

1 Inlet Inward projecting                 0.00  30.00   5.66    0.00

Elev =  132.63 meters   Press = 121.39 Kpa

2 Pipe                     l=  35.18 3.00e-002  30.00   5.66    2.83

3 Pipe  Fitt -elbow-45 deg l=   4.27 3.00e-002  30.00   5.66    0.34

4 Pipe                     l=  30.00 3.00e-002  30.00   5.66    2.41

5 Pipe  Fitt -Tee-thruflo  l=   5.79 3.00e-002  30.00   5.66    0.47

6 Pipe                     l=  15.00 3.00e-002  30.00   5.66    1.21

7 Pipe  Fitt -Tee-thruflo  l=   5.79 3.00e-002  30.00   5.66    0.47

8 Pipe                     l=  47.00 3.00e-002  30.00   5.66    3.78

9 Pipe  Fitt -Sw chk val   l=  22.86 3.00e-002  30.00   5.66    1.84

10 Pipe  Fitt -Plug Val Str l=   4.27 3.00e-002  30.00   5.66    0.34

11 Pipe                     l=   4.00 3.00e-002  30.00   5.66    0.32

12 Pump  pump prescribed for system

Elev =  125.79 meters   Press = 99.29 Kpa

13 Pipe                     l=   4.00 3.00e-002  30.00   5.66    0.32

14 Pipe  Fitt -Plug val str l=   4.27 3.00e-002  30.00   5.66    0.34

15 Pipe                     l= 150.00 3.00e-002  30.00   5.66   12.07

16 Pipe  Fitt -elbow lr 90  l=   7.62 3.00e-002  30.00   5.66    0.61

17 Pipe                     l=  85.18 3.00e-002  30.00   5.66    6.85

18 Exit                                    0.00  30.00   5.66    0.00

Elev =  178.15 meters   Press = 103.54 Kpa

SUMMARY OF PUMPING SYSTEM DATA  (System: DEMO2.FLO)

CONFIGURATION:   Darcy-Wiesbach Eq.

Flow                =       0.40 m3/sec

FLUID PROPERTIES:

Specific Gravity    =      0.860

Vapor Pressure      =       0.50 Kpa

Kinematic Viscosity =   4.1e-006 m2/sec

STATIC HEADS:

Suction Elev Head   =       6.84 meters

Discharge Elev Head =      52.36 meters

Exit - inlet press. =      -2.12 meters

Total Static Head   =      43.40 meters

NPSHA CALCULATION:

Supply pressure     =     121.39 Kpa (abs)

Vapor pressure      =       0.50 Kpa (abs)

Suction static head =       6.84 meters

Suction dynamic hd  =      14.01 meters @ design flow

NPSHA               =       7.16 meters

HEAD LOSSES (in meters)

FLOW (m3/sec)

SUCTION SIDE                  0.20        0.40        0.60

MINOR LOSSES:

Valves & fittings                       0.00        0.00        0.00

MAJOR LOSSES:

Pipe HL using Darcy-Wiesbach Eq         3.87       14.01       30.05

STATIC SUCTION HEAD:

Inlet - pump elev + pressures           9.46        9.46        9.46

TOTAL SUCTION HEAD:

Head (+), lift (-)                      5.59       -4.55      -20.59

DISCHARGE SIDE

MINOR LOSSES:

Valves & fittings                       0.00        0.00        0.00

MAJOR LOSSES:

Pipe HL using Darcy-Wiesbach            5.58       20.20       43.32

STATIC DISCHARGE HEAD:

Exit - pump elev + pressures           52.86       52.86       52.86

TOTAL DISCHARGE HEAD:

Static head plus friction losses       58.44       73.07       96.19

TOTAL SYSTEM LOSSES

TOTAL SUCTION HEAD:

Static head + friction losses           5.59       -4.55      -20.59

TOTAL DISCHARGE HEAD:

Static head + friction losses          58.44       73.07       96.19

TOTAL SYSTEM HEAD:

Suction and discharge heads            52.85       77.62      116.78

Pump Prescription:

Design operating point:  FLOW =        0.40 m3/sec

HEAD =       77.62 meters

NPSHA =       7.16 meters

APPENDIXES

Darcy-Wiesbach specific roughnesses in mm.

(Source - Pipeflow analysis by Stephenson, 1984)

Finish                               Smooth    Average      Rough

-------------------------------------------------------------------------

Glass, drawn metals                     0        0.003      0.006

Steel, PVC or AC                        0.015    0.03       0.06

Coated steel                            0.03     0.06       0.15

Galvanized, vitrified clay              0.06     0.15       0.3

Cast iron or cement lined               0.15     0.3        0.6

Spun concrete or wood stave             0.3      0.6        1.5

Riveted steel                           1.5      3          6

Foul sewers, tuberculated

water mains                      6       15         30

Unlined rock, earth                    60      150        300

COMMON CONVERSIONS

MULTIPLY              BY                  TO GET

feet                 .30480               meters

meters               3.2808               feet

psi                  6.8948               Kpa

Kpa                  .1450                psi

gpm (U.S.)           .06309               liters per second

cfs                  448.8                gpm (U.S.)

cubic meters/sec     1000.                liters per second

feet of liquid       SG/2.31              psi

psi                  2.31/SG              feet of liquid

meters of liquid     SG/.102              Kpascals

Kpascals             .102/SG              meters of liquid

centistokes          1x10-6               square meters / sec.

ATMOSPHERIC PRESSURES AT VARIOUS ALTITUDES

ALTITUDE                   PRESSURE

FEET      METERS        Psia       Kpa

-1000     -304.8        15.2     104.8

-500     -152.4        15.0     103.4

0        0          14.7     101.4

500      152.4        14.4      99.3

1000      304.8        14.2      97.9

1500      457.2        13.9      95.8

2000      609.6        13.7      94.5

2500      762.0        13.4      92.4

3000      914.4        13.2      91.0

3500     1066.8        12.9      88.9

4000     1219.2        12.7      87.6

4500     1371.6        12.4      85.5

5000     1524.0        12.2      84.1

5500     1676.4        12.0      82.7

6000     1828.8        11.8      81.4

6500     1981.2        11.5      79.3

7000     2133.6        11.3      77.9

7500     2286.0        11.1      76.5

8000     2438.4        10.9      75.2

8500     2590.8        10.7      73.8

9000     2743.2        10.5      72.4

9500     2895.6        10.3      71.0

10000     3048.0        10.1      69.6

15000     4572.0         8.3      57.2

20000     6096           6.7      46.2

30000     9144           4.4      30.3

40000    12192           2.7      18.6

50000    15240           1.7      11.7