|

|

|

|

|

|

|

|        USER'S MANUAL

|

|

|

|

|        ELECTRC Version 10

|        Shareware Evaluation Version

|

|        Copyright 1988-96, by Robert J. La Capra

|        All Rights Reserved

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|        Robert J. La Capra

|        50 Hillside Terrace

|        Andover, NJ 07821

|

|        Fax: 908-850-1612

TABLE OF CONTENTS

Disclaimer ................................................ i

Files Included On ELECTRC Disk ............................ i

Product Support Policy ................................... ii

Introduction ............................................ iii

Shareware ................................................ iv

INSTALLING AND RUNNING ELECTRC

Hard Drive or Floppy Disk ............................. 1

Setup Defaults ........................................ 1

Menu Selection ........................................ 2

Data Input ............................................ 2

CONDUCTORS and TERMINAL TEMPERATURE RATINGS ............... 3

BOX FILL & SIZING

Outlet, Device and Junction Box Sizing ................ 8

Junction, Pull Box Sizing - Straight Pull ............ 10

Junction, Pull Box Sizing - Angle or U Pull .......... 10

CONDUIT FILL ............................................. 11

GENERAL CALCS:

Cost To Operate ...................................... 12

Motor Amps When Hp, Pf, And Efficiency Are Known ..... 12

Motor Hp When Volts, Amps, Pf And Efficiency Are Known 13

Amps When Va And Pf Are Known ........................ 13

Va When Volts, Amps, And Pf Are Known ................ 13

LIGHTING CALCULATIONS (Zonal Cavity Method) .............. 14

MOTOR CALCULATIONS

Branch Conductor Sizing .............................. 17

Fuse or Breaker Sizing ............................... 17

Overload Protection Sizing ........................... 17

CONDUCTOR SIZING ......................................... 18

POWER FACTOR CORRECTION .................................. 19

PRINTING REPORTS ......................................... 21

QUICK REFERENCE TABLES

Equipment Grounding Conductors ....................... 22

Grounding Electrode Conductors ....................... 22

Killowatt - Ampere Tables ............................ 22

Underground Cover Requirements ....................... 22

Metal Device Boxes ................................... 22

Standard Pull & Junction Boxes ....................... 22

Standard Fuses & Breakers ............................ 22

Transformer Kva - Amperes ............................ 22

Terminal/Conductor Temperature Limitations ........... 23

Conductor Ampacity ................................... 23

SHORT CIRCUIT CALCS ...................................... 23

VOLTAGE DROP CALCULATOR .................................. 26

OTHER ELECTRICAL SOFTWARE AVAILABLE ...................... 28

Page i

-------------------------------------------------------------

DISCLAIMER OF WARRANTY

THIS SOFTWARE AND DOCUMENT ARE OFFERED "AS IS" AND WITHOUT

WARRANTIES AS TO PERFORMANCE OF MERCHANTABILITY OR ANY OTHER

WARRANTIES WHETHER EXPRESSED OR IMPLIED. BECAUSE OF THE

VARIOUS HARDWARE AND SOFTWARE ENVIRONMENTS INTO WHICH THIS

PROGRAM MAY BE PUT, NO WARRANTY OF FITNESS FOR A PARTICULAR

PURPOSE IS OFFERED.

GOOD DATA PROCESSING PROCEDURE DICTATES THAT ANY PROGRAM BE

THOROUGHLY TESTED BEFORE RELYING ON IT. THE USER MUST ASSUME

THE ENTIRE RISK OF USING THIS PROGRAM. THE AUTHOR OF THIS

PROGRAM ASSUMES NO LIABILITY.

DUE TO THE NATURE OF THIS PROGRAM, THE USER MUST BE FAMILIAR

WITH THE SAFETY CONSIDERATIONS OF DESIGNING AND SAFELY

INSTALLING ELECTRICAL WIRING SYSTEMS, IN ACCORDANCE WITH THE

NATIONAL ELECTRICAL CODE. THIS PROGRAM IS NOT INTENDED TO

REPLACE THE NEED FOR A QUALIFIED PERSON WHO IS EXPERIENCED IN

THE ELECTRICAL DESIGN, CONSTRUCTION AND MAINTENANCE OF SAID

ELECTRICAL SYSTEMS IN THEIR ENTIRETY.

FILES INCLUDED ON ELECTRC DISK:

Electrc.doc ... This documentation file

Electrc.exe ... Electrc program file

Electrc.dat ... Data file required by program

Electrc.rep ... Sample printed reports

NOTE:

Electrc.ini will be created by the program, and written to

the current drive/directory, if you choose 'Setup' from the

main menu and change screen display, printer port, or

formfeed. The file named ELECTRC.DAT contains data that is

used by the Quick Reference Tables. It must be located in the

same drive & directory as the program file, ELECTRC.EXE

Page ii

-------------------------------------------------------------

PRODUCT SUPPORT POLICY

Your purchase of ELECTRC software will entitle you to

extended product support services and other features which

are intended to provide you with continuous satisfaction.

If any program bugs are discovered which affect the intended

functionality or accuracy of the program, a revised program

disk will be sent to you, free of charge. Or, if you prefer,

return the original program disk for a refund, minus shipping

and handling charges.

You will automatically be notified of any upgrades and new

programs as they become available. Upgrades will be made

available to you at a special reduced fee.

You have unlimited free support via US Mail. If you have

access to the CompuServe Information Service, you also have

unlimited support via CompuServe Mail, by leaving me  a Mail

Message. My CompuServe ID#: 76417,3323. Your message will

generally be answered within 24 hours or less. No messages

will be accepted through any gateways of other electronic

mail services when postage is due, or in any case where

postage is due. For support via CompuServe Mail, supply your

serial number and your CompuServe ID# and your message.

If you purchased the optional fax support subscription for

ELECTRC, you have three years of unlimited fax support.Even

if you did not purchase fax support, you are encouraged to

fax your questions and communications to me. Return

correspondence will be via US Mail or Compuserve Mail if your

fax subscription is not in effect.

Your feedback is the most important planning and development

tool available to me. I look forward to hearing your thoughts

about the present capabilities of the software, your wish

list for additions and modifications of future versions, and

any additional ideas for making the software more useful.

Page iii

-------------------------------------------------------------

INTRODUCTION

ELECTRC Version 10 is designed to perform most common

electrical contracting and engineering calculations:

* Device, junction and pull box calcs.

* Conduit fill calculations.

* Cost to operate various loads at different kwh charges.

* Lighting calculations based on zonal cavity method.

* Motor conductor, overcurrent and overload calculations.

* Conductor sizing based on allowable voltage drop.

* Calculate:

Amps when hp, pf, and efficiency are known

Amps when va and pf are known

Va when volts, amps, and pf are known

Hp when volts, amps, pf and efficiency are known

* Quick reference tables for:

Grounding electrode & equipment ground conductor sizes

Underground cover requirements

KW to ampere tables

Transformer Kva to ampere tables

Device, pull & junction box size and capacity

Standard fuse & breaker ratings

Wire ampacity table

New terminal temp rating requirements - NEC 110-14(c)

* Voltage drop calcs.

* Short circuit calculations.

* Power factor correction.

* All functions operate with 'what-if' capability. You can

quickly and easily change only the data you wish to,

without having to start a new calculation and re-enter all

the required data. Results are calculated and displayed as

you make each change.

* Print routines for all functions. Print report to printer

or to a disk file.

* All functions conform to the 1996 National Electrical Code.

The National Electrical Code is a copyrighted document of the

National Fire Protection Association, Batterymarch Park,

Quincy, MA. 02269. RUNNING ELECTRC

Page iv

-------------------------------------------------------------

SHAREWARE:

'Shareware' is a term used to describe a system of distribution

for software. Under the shareware concept, you may use this

Shareware Evaluation Version for a short trial period to

determine if it meets your needs. If it does, you register with

the author of the software and pay a registration fee. This

registration grants you the right to retain the software for

your continued use. If the software does not meet your needs,

and you do not register it, you must stop using it.

The shareware system provides substantial benefits:

1) You get to try out the software BEFORE you buy it, so you

know what you are buying.

2) Shareware is substantially less expensive than comparable

commercial programs. You don't pay for costly marketing

and advertising programs.

3) Upon your registration, you receive the latest version of the

program, with additional functions and features.

The system is based entirely on the honor system, and generally

works quite well.

Shareware is NOT free software. The author counts on your

integrity. If you continue to use this software, you must

register directly with the author by using the 'Print

Registration Form' function of the program (from the main menu,

select QUIT, then select PRINT REGISTRATION FORM).

Upon your registration, you will receive:

1) The latest version of this software, with all the functions

described in this documentation file. Note that this shareware

evaluation version is not a demo or a crippled version. It is

a fully functional program. The version that you will receive

with registration is an expanded version, with added features.

This documentation file describes all the features of the

expanded version so that you can see what you will be buying.

2) A single-user license granting you the right to retain the

software and to continue using it.

3) Unlimited free technical support.

4) Automatic notification of future upgrades, and greatly reduced

registration fees for all upgrades.

5) Eternal gratitude from this author for your support of his

tireless development efforts.

You may make copies of this shareware evaluation version and give

them away to colleagues, friends, etc, as long as:

1) You do not receive any financial compensation for doing so.

2) You include ALL files included on this shareware evaluation

diskette, not modified in any way.

3) The receivers understand the shareware concept, understand

that this is NOT free software, and agree to obide by the

terms and conditions stated above.

Page 1

-------------------------------------------------------------

INSTALLING AND RUNNING ELECTRC

Hard Drive ( Recommended )

ELECTRC will run more quickly from a hard drive since some of

the functions access the disk to read-in external files.

First copy all files from the ELECTRC disk to the hard drive.

Then from the DOS prompt, type ELECTRC then press ENTER.

Floppy Disk

Insert the ELECTRC disk into the disk drive (A or B), and at

the DOS prompt type ELECTRC then press ENTER.

SETUP

Display

Initially the program starts up in black and white. Select

'Setup' from the main menu. Then select either Color Display

or Mono Display, and press ENTER. You can also press the

letter key that is highlighted for the selection you want. A

checkmark at the beginning of the menu field indicates that

this field is the default. The selection takes place

immediately and is automatically saved to ELECTRC.INI file.

Printer Port

To set the printer port (LPT1 or LPT2) that the program will

send printed reports to, select 'Setup' from the main menu.

Then select either Printer Port LPT1, or Printer Port LPT2

(depending on which port your printer is connected to), and

press ENTER. You can also press the letter key that is

highlighted for the selection you want. All printed reports

will subsequently be sent to the selected port. A checkmark

at the beginning of the menu field indicates that this field

is the default. The selection takes place immediately and is

automatically saved to the ELECTRC.INI file.

Printer Formfeed

This option is useful for laser printers. If the  printed

reports do not automatically eject from your printer, you can

tell this program to force a page-eject. Select 'Setup' from

the main menu. Then select 'Add Printer FORMFEED', and press

ENTER. You can also press the letter key that is highlighted

for the selection you want. A checkmark at the beginning of

the menu field indicates that this field is the default. This

menu field operates as a toggle. If presently selected

(checkmark), selecting it again will turn it off (no

checkmark). The selection takes place immediately and is

automatically saved to ELECTRC.INI file.

Page 2

-------------------------------------------------------------

MENU SELECTION

The main menu is a pull down type, structured as a horizontal

bar at the top of the screen with main titles displayed. Each

of these main titles represents a sub menu with one or more

related program functions.

To select specific program functions:

1. Press the hilighted letter of the menu item (main or sub).

OR,

2. Press the DOWN ARROW key to open the first sub menu, then

use LEFT or RIGHT ARROW keys to move between sub menus.

OR,

3. Position the hilighted block over a menu selection (main

or sub), then press ENTER.

DATA INPUT

All functions operate with 'What-If' data entry routines.

This allows you to instantly see the results of changing one

data item at a time. You will not need to restart the

function from the beginning just to see the effect of

changing one item.

Data input routines are similar in all functions. Use the UP,

DOWN, or ENTER keys to move between input fields, entering

data as you go. Some fields limit your input to certain

values, and if you input data that is unacceptable, you will

hear a beep and will not be able to move from that field

until the correct data has been entered (or leave the field

empty).

Some functions require that you select one data item from a

list. This is done by pressing a function key which pops up a

menu where you will select one item from a list of choices.

Use the UP or DOWN ARROW keys to position the hilighted bar

over your choice and press ENTER. After you have entered all

required data, the calculation will be performed and

displayed. You can then change individual data items and

instantly see the results.

CAUTION:

When entering the last data item, or changing one data item

which was previously entered: Be sure to record that change

by moving from that field to another field, or by pressing

ENTER while still on that field.

Page 3

-------------------------------------------------------------

CONDUCTORS and TERMINAL TEMPERATURE RATINGS

ELECTRC Version 10 supports ampacity correction and

adjustment, and the NEC 110-14(c) temperature limitation

requirements.

*** NOTE ***

This program will allow you to input values of 60, 75, or 90

degrees C for terminal temperature ratings. The 90 degree

rating is rarely (if ever) found (so far). It is here for

flexibility reasons only. YOU MUST ASCERTAIN the actual

listed terminal temperature rating of your equipment before

selecting one of the three possible ratings in this program.

NEC Section 110-14(c) specifies that terminal temperature

ratings are related to circuit ratings and listed equipment

terminal conductor size ranges. It restricts terminations of

equipment to: 60 degrees C for circuits of 100 amps or less

or for equipment terminals rated for Numbers 14 through 1

conductors; and 75 degrees C for circuits greater than 100

amps or for equipment terminals rated for greater than Number

1 conductors.

It also provides exceptions for conditions where the listing

and labeling of certain equipment allows higher terminal

temperature ratings. For reasons of flexibility, this program

supports the use of these NEC exceptions.

It is your responsibility to select terminal temperature

ratings (60/75/90 degrees C) according to the actual ratings

of your equipment. This rating can be found stamped on the

equipment, or on the product label.

It is also your resonsibility to understand the requirements

of NEC Section 110-14 before using the Conductor Sizing or

Motor Calcs functions of this program.

************

You may be wondering why this section of the documentation is

so lengthy. There is a VERY good reason. If YOU fail to pay

careful attention to conductor and terminal temperature

ratings, YOU will be held accountable to YOUR client for

equipment and/or other losses! Whether you use this program

or pen and paper for your calculations, you must be fully

aware of the safety benefits, or, the potential for serious

damage. My intent here is not to scare you. It is to

emphasize the importance of understanding how this program

sizes conductors, and the importance of the type of input

that you supply to the program.

Page 4

-------------------------------------------------------------

ELECTRC is valued for its ease of use, its ability to perform

complex calculations, and its consistent accuracy. In order

for you to reap these benefits from the program, you must be

aware of the safety requirements of conductor and termination

temperature coordination.

Flexibility has been incorporated into this program. In both

the Conductor Sizing and Motor Calc functions of this

program, you will select from a number of different conductor

types, and you will select from several different terminal

temperature ratings. The program will, for example, allow you

to select a terminal temperature rating of 90 degrees C.

Again, this is made possible for reasons of flexibility. Few,

if any (yet) terminals are rated for this high temperature.

Unless you are CERTAIN that ALL the terminals of the

equipment which will be connected to a conductor supplying

that equipment are rated for this high temperature, you

should not select it. Common terminal temperature ratings are

60 or 75 degrees C.

NEC Section 110-14 spells out this requirement clearly. You

should read this section of the NEC before proceeding. Also

be aware that temperature rating limitations apply throughout

all conductor runs--from termination to termination, and also

to any splices or taps anywhere along these runs (yes, this

applies even to wirenuts).

The full text of NEC Section 110-14(c) can be viewed from

within the program. This text is viewable by pressing the F1

key from within the Conductor Sizing and Motor Calcs

functions, and by selecting it from the Quick-Reference

Tables submenu which is accessable from the main menu. See

the Quick-Reference Tables section of this documentation for

details.

Please study this section carefully before using the

Conductor Sizing or Motor Calcs functions. Your efforts here

will bear dividends throughout your long and beneficial

relationship with ELECTRC software. We will continue this

discussion by reviewing the knowledge that you already

possess about conductors and heat flow. Then we will apply

that knowledge to the coordination of conductors and

terminations.

Current flowing through a conductor produces heat as a side

effect. Excessive heat will degrade the conductor's

insulation and the conductor material. The allowable

ampacities listed in NEC Table 310-16 take this into

consideration, and indicate the maximum ampacity that each

listed conductor can carry continuously without being

overheated. These allowable ampacities are valid only when

the conductor is operating in a 30 degree C environment, and

when not more than three current carrying conductors are

contained within a cable, raceway or in the earth.

Page 5

-------------------------------------------------------------

When a conductor operates in an ambient temperature other

than 30 degrees C, the allowable ampacity of that conductor

must be adjusted according to the ambient temperature

correction factors listed at the foot of NEC Table 310-16.

For example, according to Table 310-16, a number 6awg type

thhn copper conductor with 90 degree C insulation can

continuously carry 75 amperes in an ambient temperature of 30

degrees C., with not more than two additional current

carrying conductors within the same raceway. Under these

conditions, the conductor would reach, but not exceed, 90

degrees C. The conductor would not be damaged. For an ambient

temperature of 45 degrees C, however, the heat will not be

carried away from the conductor quickly enough to prevent

damage. Here we would have to limit the amperage (and heat

generation) carried by this conductor to prevent it from

being damaged. We do this by multiplying the 75 ampere rating

of this conductor by the ambient temperature correction

factor of .87 from Table 310-16. This conductor now has an

ambient temperature corrected ampacity of 75 x .87 = 65.25

amperes. This represents the maximum load that it can safely

carry continuously.

When more than three current carrying conductors are in close

proximity within a closed container, heat generation is

increased, heat dissipation is decreased, and a potential for

exceeding a conductor's design temperature is created. Note 8

to Table 310-16 mandates that the allowable ampacity of all

the current carrying conductors contained in the raceway,

cable or earth must be adjusted according to the adjustment

factors listed in the note. For example, if a number 6awg

thhn copper conductor with 90 degree C insulation is

installed in a raceway with three additional current carrying

conductors, note 8 mandates that we multiply the allowable

ampacity of 75 amperes by the adjustment factor of 80%. This

yields a corrected ampacity of 75 x .8 = 60 amperes.

If the above conductor was installed in an ambient

temperature of 45 degree C, along with three additional

current carrying conductors in a raceway, then both the above

correction and adjustment factors would need to be applied.

This would yield a corrected ampacity of 75 x .87 x .8 = 52.2

amperes.

ELECTRC Version 10 performs both these ampacity corrections

and adjustments based on the conductor type, ambient

temperature, and circuit type that you select. When you press

the function key which pops up a list of available conductor

types, you will see a location reference (wet, dry, etc), and

a maximum conductor operating temperature rating (60, 75, 90

degree C) associated with each conductor. When you select a

conductor type from the list, you are also choosing the

maximum operating temperature of that conductor (which column

of Table 310-16 will be referenced for allowable ampacity).

Page 6

-------------------------------------------------------------

As an example of how the program selects the correct

conductor size, consider the circuit below where you input

the following data for a load to be served:

Full Load Amps:      137

Load Type:      Noncontinuous

Ambient Temp:      31-35 Deg.C

Conductor:      Type THHN Copper  -  Dry  -  90 Deg.C

Ambient Temp:      41-45 Deg.C

Circuit Type:      3 Phase 4 Wire Y, Harmonic Load

Terminal Temp:      75 Degrees C

1.     It reads the value that you input for load amperage.

2.     The load is noncontinuous (does not operates for 3

hours or more), so it multiplies the load amperage by

100%. (137 x 1.0 = 137.0 amps).

3.     It reads the ambient temperature that you have

selected, and multiplies the above cumulative product

by the reciprocal of the ambient temperature

correction factor of .96. (1/.96=1.04).

(137.0 x 1.04 = 142.48 amps).

4.     Since the neutral in this circuit type carries

current, there are 4 current carrying conductors. The

above cumulative product is multiplied by the

reciprocal of the correct adjustment factor of 80% as

per NEC Note 10. (1/.8=1.25).

(142.48 x 1.25 = 178.1 amps).

5.     At this point the program has calculated the conductor

ampacity (178.1) that is required to serve the load.

Now the program searches the 90 deg.C temperature column of

NEC 310-16 (based on your conductor selection of type thhn,

dry location, 90 deg.C max operating temperature) to find a

conductor size that has an allowable ampacity of at least

178.1. A #2/0 conductor, with an allowable ampacity of 195

amperes is selected.

Next the program performs a verification test to assure the

accuracy of its work:

1.     NEC Table Ampacity x ambient temperature correction

factor x number of current carrying conductors

adjustment factor = maximum allowable ampacity.

(195 x .96 x .8 = 149.76 amps). This is sufficient to

serve the load of 137 amps.

Once the correct conductor size has been selected, and the

program has verified its work, the next step is to assure

that the selected conductor will not overheat the terminal to

which it is attached. The program takes care of this

automatically. Before describing this process, we will

discuss the requirements of the termination.

Page 7

-------------------------------------------------------------

In the above example calculation, a #2/0 thhn conductor with

a maximum operating temperature of 90 degrees C was selected

to satisfy the conductor requirements of the example load.

After correction and adjustment factors were applied, the

conductor had an allowable ampacity of 149.76 amperes. This

means that for the ambient temperature and number of current

carrying conductors in the example, this #2/0 conductor can

continuously carry 149.76 amperes without being damaged. When

carrying 149.76 amperes under these conditions, this conductor

will reach, but not exceed, its 90 degree C design

temperature rating. It will not be damaged. The terminal to

which it is connected, however, might be.

Most equipment terminals are rated at either 60 degrees C, or

75 degrees C. Some are dual rated at 60/75 degrees. What this

means is that the rated temperature of the terminal cannot be

exceeded without damage to the terminal itself or to the

equipment connected to the terminal.

At this point in the conductor selection process, we have to

stop and consider a potentially serious problem. The selected

conductor will be carrying 137 amperes, and since this value

is close to the conductor's adjusted maximum allowable

ampacity, this conductor's temperature along the conductor

run will approach some value close to 90 degrees C. In the

example above, you input a value of 75 degrees C for the

terminal temperature rating. This conductor, serving this

load, could deliver close to 90 degrees of heat into the 75

degree rated terminal/equipment to which it is connected!

What we need to do next is to calculate the maximum ampacity

(heat) that this terminal can safely carry. The program does

this automatically for all conductor sizings. This is the

method used by the program for the above example load:

1.     The load amperage = 137.

2.     Noncontinuous load = 137 x 1.0 = 137 amps.

3.     The required termination ampacity is 137 amps at 75

degrees C (the terminal temp rating you supplied).

Now the program searches the 75 deg.C temperature column of

NEC 310-16 to find a conductor size that has an allowable

ampacity of at least 137 amperes. Note that no correction or

adjustment factors apply at the terminal. They only affect

the conductor run. A #1/0 conductor, with an allowable

ampacity of 150 amperes, is selected.

Next the program performs a verification test (as performed

for the conductor run above) to assure the accuracy of its

work. Here, however, it does not include the correction or

adjustment factors.

Page 8

-------------------------------------------------------------

The next-to-final step in the program's selection process is

the comparison of the two conductors selected so far. Both

conductors selected--the #2/0 and the #1/0--are compared, and

the worst case (the larger conductor size) is finally

selected. This is the #2/0 conductor.

The final step is one additional verification test to assure

the satisfaction of both requirements. The #2/0 conductor

satisfies the requirements of both the conductor run and the

termination.

DEVICE, OUTLET AND JUNCTION BOX FILL

Determines cubic inch volume required for outlet, device and

junction boxes, as per NEC section 370-16. Conductor size

range is from #18 thru #6.

A separate volume calculation is made for each of the

following, and then these volumes are added together. This

total volume determines the minimum cubic inch volume

capacity that a box must contain. All the following volume

calculations are based on NEC Table 370-16(b):

Conductors:

Each conductor originating outside the box and terminates or

is spliced within the box is counted once. Each conductor

that passes through the box without termination or splice is

counted once. Conductors, no part of which leaves the box,

are not counted. A conductor fill volume is calculated by

adding these individual volume requirements.

Clamp Fill:

Where one or more internal cable clamps, either factory

installed or field installed, are present in a box, a single

volume allowance is made based on the largest conductor in

the box. Cable connectors (bx, romex connectors) with their

clamping mechanism outside the box are not counted.

Support Fittings:

Where one or more fixture studs or hickeys are present in a

box, a single volume allowance is made for each type of

fitting, based on the largest conductor in the box.

Devices Or Equipment:

For each yoke or strap containing one or more devices or

equipment, a double volume allowance is made for each yoke or

strap based on the largest conductor connected to each yoke

or strap.

Page 9

-------------------------------------------------------------

Equipment Grounding Conductors:

Where one or more equipment grounding conductors enter a box,

a single volume allowance is made based on the largest

equipment grounding conductor in the box. Where an additional

set of such conductors (isolated ground conductors, for

example) are present in a box, an additional volume allowance

is made based on the largest grounding conductor of this set.

NEC Table 370-16(b)

Volume Allowances of Conductors

---------------------------------------------------

# 18 .. 1.50   |    # 12 .. 2.25   |    #  6 .. 5.0

# 16 .. 1.75   |    # 10 .. 2.50   |

# 14 .. 2.00   |    #  8 .. 3.00   |

Data Input:

Enter The Quantity Of Each Size Conductor Within The Box:

A conductor running thru the box with no splices or

connections within the box should be counted as 1 conductor.

A conductor originating outside the box and terminating

within the box should be counted as 1 conductor.

Conductors, no part of which leaves the box (example ... a

jumper or pigtail from a splice within the box to a switch,

outlet or fixture mounted on the box), should not be counted.

Answer the prompts for devices, clamps, fittings, ground

conductors, and additional ground conductors:

Count each mounting yoke or strap containing one or more

devices as 1. Example... one duplex outlet - count as 1. two

duplex outlets - count as 2.

The remaining prompts are self explanatory. Answer Y for yes.

There is no need to answer N for any prompts which would be

answered as 'no'. A blank field is interpreted as 'no'.

A quick reference table of standard metal boxes and their

cubic inch capacity is available for viewing at any time, by

pressing F2. The current screen will be saved, and the table

will be shown. When you wish to return to the previous

screen, press any key. You will be returned to the data entry

screen with all previously entered data intact.

A printout is available by pressing F10. See the

documentation for printing for details.

Page 10

-------------------------------------------------------------

JUNCTION & PULL BOX SIZING - Straight Pull

Calculates the minimum length, in inches, of pull and

junction boxes where raceways enter and leave the box at

opposite ends. If the wiring method is cable assemblies

instead of raceways, first determine the trade size conduit

which would be appropriate for the size and quantity of

conductors in the cable assembly, then use that conduit size.

If more than one raceway or cable enters and/or leaves either

end of the box, always use the largest size.

Method used to determine minimum box length for straight

pull:

Eight times the trade diameter of the largest raceway.

The operation of this function is straightforward. Position

the hilighted bar over the largest raceway size for this

calculation, then press ENTER. The results will be displayed.

A printout is available by pressing F10. See the

documentation for printing for details.

JUNCTION & PULL BOX Sizing - Angle or U Pull

Calculates the minimum distance, in inches, between each

raceway entry inside a junction or pull box and the opposite

wall of the box, where raceways enter and leave the box at

angles. If the wiring method is cable assemblies, see the

explanation above, under 'Straight Pull'.

The method used to determine minimum distance for angle or U

Pull:

Six times the trade diameter of the largest raceway, PLUS,

the sum of the diameters of all other raceway entries in

any one row on the same wall of the box. Use the row with

the largest total diameter of raceways.

A quick reference table of standard boxes and their cubic

inch capacity is available for viewing at any time, by

pressing F2. When you wish to return to the previous screen,

press any key. A printout is available by pressing F10.

Page 11

-------------------------------------------------------------

CONDUIT FILL

The Conduit Selector allows you to quickly and accurately

determine the minimum conduit size required for 1 or more

conductors. Calculations are based on the Dimensions and

Percent Area of Conduit and Tubing from table 4 (12

individual raceway types), and from Conductor Dimensions as

per Table 5 and Table 8 of the NEC.

The maximum allowable percentage of conduit fill as per NEC

Table 1 is:

53% for 1 conductor;

31% for 2 conductors;

40% for more than 2 conductors,

Data Input:

Use the UP, DOWN, TAB or SHIFT+TAB keys to move the cursor to

the desired wire size/type position, then enter the quantity

of that size/type conductor to include in the conduit. If you

want to include other size/types of conductors into the same

conduit, then repeat the above procedure. You can enter any

combination of conductors in the same conduit.

NOTE: Several fields will show an asterisk ( * ). This

represents the unavailability of these sizes/types of

conductors. These fields cannot be altered.

F3 brings up a pop-up menu where you will select a raceway

type. Use the up or down cursor keys to position the

hilighted bar over your choice, then press ENTER.

F2 brings up a screen report showing the results of the

calculation.This feature becomes available after entering one

or more conductors and after selecting a raceway type. The

program will list all the sizes and types of conductors you

chose for the calculation, their individual areas, the total

area of all selected conductors, the total 100% area of the

selected raceway type, the maximum allowable percentage fill

of the raceway, the minimum trade size conduit required, and

the percent conduit fill for the calculation.

If more data is available than will fit on the screen, you

will be able to use the UP and DOWN ARROW keys to scroll

through the data. Pressing any other key will return you to

the conduit selector input screen with all previous data

intact.

F10 allows you to send a printout to the printer or disk

file. See the PRINTING section of this documentation for

details.

Page 12

-------------------------------------------------------------

GENERAL CALCULATIONS:

Cost To Operate

Calculates the cost to operate a certain load a number of

hours daily for some number of days at a certain KWH utility

charge.

POWER OF LOAD is the number of watts the load draws. DAILY

USE is the number of HOURS the load is operated per day.

NUMBER OF DAYS is the number of days the load is operated.

PRICE / KWH is the utility charge per killowatt hour.

(Example..  10 cents/kwh, enter .10)

NOTE: A value of ten cents/Kwk initially appears in the

'Price/Kwh' field, as an example only. You should change this

value to reflect your own price/Kwh charge.

After entering the above information, the program calculates

and displays the cost to operate the load for the number of

hours daily for the number of days at the chosen utility

charge. A printout is available by pressing F10. See the

documentation for printing for details.

Motor Amperes

A generic procedure to calculate motor amperage when hp, pf

and efficiency are known.

The calculation formula is:

Single phase:

(hp x 746) / (volts x pf x efficiency)

Three phase:

(hp x 746) / (1.73 x volts x pf x efficiency)

Simply enter appropriate values at the prompts for hp, pf and

eff. If pf and/or eff. is 100% or unity, enter 100 at those

prompts. Note that this procedure is not to be used in

determining motor full load amperage for the purpose of

calculating conductor, overcurrent or overload sizes. Use the

'Motor Calcs' function.

Page 13

-------------------------------------------------------------

Motor HP

A generic procedure to calculate motor horsepower when

voltage, amperage, pf and efficiency are known.

The calculation formula is:

Single phase:

(volts x amps x pf x efficiency) / 746

Three phase:

(1.73 x volts x amps x pf x efficiency) / 746

Simply enter appropriate values at the prompts for volts,

amps, pf and eff. If pf and/or eff. is 100% or unity, enter

100 at those prompts.

Amperes

Used to calculate amperes when va and volts, and pf are

known.

The formula is:

Single phase:

va / (volts x pf)

Three phase:

va / (1.73 x volts x pf)

Simply enter appropriate values at the prompts for va, volts

and  pf. If pf is 100% or unity, enter 100 at that prompt.

Va

Used to calculate va when volts, amps and pf are known.

The formula is:

Single phase:

volts x amps x pf

Three phase:

1.73 x volts x pf

Simply enter appropriate values at the prompts for volts,

amps and  pf. If pf is 100% or unity, enter 100 at that

prompt.

Page 14

-------------------------------------------------------------

LIGHTING CALCULATION ( Zonal Cavity Method )

Calculates the quantity of lighting fixtures required to

light any room or area to any desired footcandle level.

ELECTRC Version 10 includes some of the popular new lamp

types mandated by the Federal Energy Act. The inclusion of

all possible lamp and fixture types would require a separate

program several times the size of this one. This is not

required. This program allows you to specify ANY fixture

and/or lamp type by entering the CU of the desired fixture or

the lumen quantity of the desired lamp. The program will then

perform the calculation as if this fixture/lamp were in its

internal database. First some background.

The Illuminating Engineering Society (IES) has devised a

flexible and accurate method for calculating lighting

requirements, called the ZONAL CAVITY METHOD. This method

assumes that any room or area to be lighted is made up of

three cavities, the CEILING CAVITY, the ROOM CAVITY, and the

FLOOR CAVITY. The CEILING CAVITY extends from the ceiling

surface down to the lighting fixture mounting level. If the

lighting fixtures are recessed or surface mounted then the

value of the Ceiling Cavity will be zero. If they are

suspended some distance below the ceiling then the value of

the Ceiling Cavity is the volume of space between the ceiling

surface and the fixture mounting level.

The ROOM CAVITY extends from the fixture mounting level down

to the work height level. The work height level is the

distance above the floor where the required quantity of

footcandles is to be maintained (usually desktop or work

bench level).

The FLOOR CAVITY extends from the work height level down to

the floor. If the required footcandles is to be maintained

all the way to the floor, then the Floor Cavity value will be

zero. Every surface exibits a certain ability to reflect

light. Light colored surfaces reflect more light than dark

surfaces, so more light will need to be provided in a dark

environment. The degree of a surface's reflectivity is

referred to as it's Percent Reflection value. Percent

Reflection can be accurately measured with a reflectometer,

or standard reflectance tables can be referred to, such as

the following:

Page 15

-------------------------------------------------------------

TABLE FOR INTERIOR ILLUMINATION DESIGN

-------------------------------------------

COLOR                % REFLECTION

-------------------------------------------

Flat white               75 - 85

Ivory                    70 - 75

Buff                     60 - 70

Yellow                   55 - 65

Light tan                45 - 55

Light green              40 - 50

Gray                     30 - 50

Blue                     25 - 35

Red                      15 - 20

Dark brown               10 - 15

------------------------------------------

The MAINTENANCE FACTOR is a value determined from the

anticipated maintenance of the fixtures and reflective

surfaces in the room or area. The intensity of illumination

produced by a lighting installation will depreciate after

some time due to lamp aging, and dust and dirt buildup. The

MAINTENANCE FACTOR is designed to adjust for this. Typical

values are from .5 to .8. (.5 for a poorly maintained

environment, .8 for well maintained).

Each lighting equipment manufacturer publishes data for the

COEFFICIENT OF UTILIZATION (CU) for each fixture type and

size in it's line. The CU of a fixture is a measure of it's

efficiency under specific conditions of room cavity values

and effective reflectance values.

The formulas used in the ZONAL CAVITY METHOD :

CEILING CAVITY RATIO = (5 * Hc (L + W)) / (L * W)

ROOM CAVITY RATIO =  (5 * Hr (L + W)) / (L * W)

FLOOR CAVITY RATIO = (5 * Hf (L + W) / (L *  W)

WHERE:

Hc = distance from ceiling to fixture level (in feet).

Hr = distance from fixture level to work height (in feet).

Hf = distance from work height to floor (in feet).

L = length of room in feet.

W = width of room in feet.

ROOM LENGTH and ROOM WIDTH values must be entered in FEET.

Decimal points are accepted (Ex. 125, 50.5, etc...).

CEILING HEIGHT and FIXTURE HEIGHT must also be entered in

FEET. Decimal points are acceptable.

WORK HEIGHT must also be entered in FEET. Decimal points are

acceptable. If you want the WORK HEIGHT to be equal to the

floor, simply enter zero.

Page 16

-------------------------------------------------------------

FOOTCANDLE LEVEL is a measure of the intensity of light

falling upon a specific surface.

Values for Percent CEILING, WALL, and FLOOR Reflectances must

be entered as whole numbers (50, 80, etc...) Exact values can

be obtained by use of a reflectometer, or a standard table

for interior illumination design can be referred to, such as

the table for interior illumination design on the previous

page.

The value entered for MAINTENANCE FACTOR must be less than or

equal to 1. The value of between .5 and .8 will be accurate

for nearly all calculations. A value of 1 will exclude the

MAINTENANCE FACTOR from the lighting calculation.

NOTE: A value of .8 initially appears in the 'Maintenance

Factor' field, as an example only. You can change this value

to reflect your own conditions.

To select fixture type, press F2. The menu will ask you to

select either 'built-in fixture type' or 'specify fixture

type'.

Built-In:

Fixture types stored internally include Recessed

Incandescent, Fluorescent, and High Intensity Discharge.

COEFFICIENT of UTILIZATION (CU) values which have been

compiled by IES are stored internally for these fixtures. The

internally stored fixtures are representitive of their types,

as are the internally stored lamp types. You will get

accurate results using them, but if you wish to use a type of

fixture not available internally, you can choose to specify

your own type.

Specify:

If you choose to specify your own fixture type, you will be

prompted for the number of lamps per fixture, the quantity of

lumens per lamp, and, the coefficient of utilization (CU) of

the fixture. You will need to have the fixture manufacturer's

CU specs. LUMEN specs are available from various sources.

Lamp manufacturers will have lamp catalogs which will list

LUMEN values for their line of lamps.

After all data has been entered, the number of fixtures

required will be calculated and displayed. A printout is

available by pressing F10. See the documentation for printing

for details.

Page 17

-------------------------------------------------------------

MOTOR CALCULATIONS

Branch Conductor Sizing

Calculates motor branch circuit conductor size as per NEC

Article 430, Part B, and 430-6.

Conductor ampacity is based on 125 percent of motor full load

amperage (as determined from NEC Table 430-148 or 430-150).

If applicable, an ambient temperature correction factor is

applied, and the product yields the conductor ampacity

required.

The process of conductor size selection is fully described in

the 'CONDUCTORS and TERMINAL TEMPERATURE RATINGS' section of

this document. Refer to it for details. The only difference

is that here in the Motor Calcs, the 'Load Amperage' is

determined from NEC Tables built into the program. Various

conductor types/temperature ratings are supported.

Fuse or Breaker Sizing

Calculates rating or setting of motor branch circuit

overcurrent protective device (Nontime-delay fuse, Time delay

fuse, Instantaneous trip circuit breaker & Inverse time

circuit breaker). NEC Article 430-Part D, and, 430-52.

Rating or setting is based on Full load amperage (from table

430-148 or 430-150) of motor, multiplied by appropriate

percentage factor from NEC Table 430-152 for the selected

motor type. NEC Article 430-52.

If this results in a value other than a standard size or

rating of overcurrent protection device, the next higher

standard rating is presented in addition to the actual

calculated val;ue. Article 430-52(a), Exception 1.

Overload Protection Sizing

Calculates motor overload protective device rating. Article

430, Part C.

Rating is based on motor full load amperage (from motor

nameplate) multiplied by:

125% if nameplate service factor is not less than 1.15,

or

125% if nameplate temperature rise is not over 40 degrees C.,

or

115 % for all others.

Page 18

-------------------------------------------------------------

Access Keys Used To Select Motor Parameters:

Press:    To Select:

--------------------------------------

F1        Help

F2        Motor Type/Phase/Voltage/Hp

F3        Wire Type

F4        Ambient Temperature

F5        Overcurrent Type

F10       Print Report

CONDUCTOR SIZING:

Calculates the conductor size required to carry a certain

load for some distance while not exceeding a specific voltage

drop percentage.

The process of conductor size selection is fully described in

the 'CONDUCTORS and TERMINAL TEMPERATURE RATINGS' section of

this document. Refer to it for details. Various conductor

types/temperature ratings are supported.

Ambient temperature derating of conductor ampacities is

fully supported.

Conductor ampacity derating due to the number of current

carrying conductors in the raceway or cable is fully

supported.

Six circuit types are supported:

1 Phase 2 Wire(Phase & neutral, or 2 Phase conductors)

1 Phase 3 Wire(2 Phase conductors & neutral)

1 Phase 3 Wire(Above circuit from a 4 wire wye system)

3 Phase 3 Wire(3 phase conductors)

3 Phase 4 Wire Wye(3 phase conductors & neutral)

3 Phase 4 Wire Wye circuit with the majority of load harmonic

In the third circuit type above, the neutral will carry

substantial current, and will be considered as a current

carrying conductor, as per NEC 310-16 Note 10(b).

In the last circuit type above, the neutral will carry

harmonic currents, and will be considered as a current

carrying conductor, as per NEC 310-Note 10(c).

Data Input

The 'Maximum Percent Of Voltage Drop' field will only accept

whole numbers in the range of 0 to 9. This will be the

maximum percentage of the supply voltage which can be dropped

by the circuit conductors. If you enter 0 in this field,

voltage drop will not be considered in the selection of the

conductor size.

Page 19

-------------------------------------------------------------

Full Load Amperage Of Load is the rated or maximum amperage.

Source Voltage is the supply voltage for the circuit.

Length of Run In Feet is one way length from supply to load.

Continuous/Noncontinuous specifies whether the full load

amperage operates for 3 hours or more (continuous) or not.

Terminal Temperature Rating is the rating applied to the

conductor termination (lug, screw terminal, etc) of the load

equipment. Refer to the 'CONDUCTORS and TERMINAL TEMPERATURE

RATINGS' section of this document for details.

Note: When you choose to include a maximum voltage drop

paramater in the conductor size selection calculation: The

program follows the procedure described in the 'CONDUCTORS

and TERMINAL TEMPERATURE RATINGS' section of this document,

and performs additional calculations to assure that the

selected conductor size will also meet the requirements of

the maximum voltage drop percentage that you input.

Access Keys Used To Select Circuit/Conductor Parameters:

Press:    To Select:

-----------------------

F1        Help

F2        Circuit Type

F3        Wire Type

F4        Ambient Temperature

F10       Print Report

POWER FACTOR CORRECTION

Calculates the existing power factor and the capacitance

required to achieve a new power factor. The calculations are

accurate for single phase & balanced three phase conditions.

Do not rely on these calculations for situations where

several loads operate independently on the same feeder or

branch circuit, because the total power factor on the feeder

or shared branch circuit will vary, depending on which loads

are operating. Instead, run a calculation for each load

independently. Then, the calculated Kvars of capacitance

required should be installed as close as possible to the

individual load for which the calculation is performed. Also

note that if you improve the power factor of an existing

Before considering the use of capacitance to improve power

factor, motor, the overload heaters should be changed to

protect the motor at the reduced amperage which will result.

determine if the low power factor condition is caused by the

use of a motor that is oversized for the driven load.

Replacing the motor with a more efficient, properly sized

unit may be more practical and cost effective.

Page 20

-------------------------------------------------------------

Power factor is the ratio of the true power (in watts) to the

apparent power (in voltamps). True power is measured with a

wattmeter. Apparent power is the product of volts and amps.

The result is the power factor of the load. For example, a

load is measured with a wattmeter and indicates 1880 watts.

The measured voltage is 240 volts. The measured current is 10

amps:

True Power         1800       1800

Power Factor = --------------- = ---------- = ------ = .75

Apparent Power    240 x 10     2400

The power factor of this load is calculated to be .75 (75%).

The apparent power (delivered power) of this load is 2400 VA

but the true power (useful power) is only 1800 watts. The

remaining 600 va are wasted in the form of heat losses.

Increasing the power factor would reduce the heat loss and

reduce the current requirements of the circuit supplying this

load.

To increase the power factor of an inductive load,

capacitance can be connected to the load. The required amount

of capacitance (in Kvars) must be calculated.

The formula for determining existing PF and capacitance

required:

Single Phase - Existing:

Kva = (volts x amps) / 1000

PF  = Kw / Kva

Phase Angle = The angle that has a cosine equal to the PF

Kvars = Kva x SIN of the phase angle

Single Phase - Proposed:

Kva = Kw / Proposed PF

Line Amps = (Watts x 1000) / (Proposed PF x Volts)

Phase Angle = Angle with a COSINE equal to the proposed PF

Kvars = Proposed Kva x SIN of the proposed phase angle

Three Phase - Existing:

Kva = (volts x 1.73 x amps) / 1000

PF  = Kw / Kva

Phase Angle = Angle with a COSINE equal to the PF

Kvars = Kva x SIN of the phase angle

Three Phase - Proposed:

Kva = Kw / proposed PF

Line Amps = (Kw x 1000) / (Proposed PF x volts x 1.73)

Phase Angle = Angle with a COSINE equal to the proposed PF

Kvars = Proposed kva x SIN of the phase angle

Single and Three Phase:

Capacitive Kvars Required = Existing Kvars - Proposed Kvars

Recovered Distribution Losses = Existing Kva - Proposed Kva

Page 21

-------------------------------------------------------------

NOTE:

Depending on computer processor speed, there will be some

delay in calculating the phase angles and the kvars. On a

486/33, it will be unnoticeable, while on an 8087 at 4.77 Mhz

it can take 15 seconds or so.

PRINTING REPORTS

You can print reports either to a printer or to a disk file

for all functions except for a few of the simpler general

calcs. All Quick Reference Tables can also be printed.

Also supported is the printing of reports to an ASCII disk

file, for importing into your word processing program. For

the general calcs, you con do a 'Print Screen' to send output

to the printer. This can be done on most computers by

pressing the SHIFT key and the PRINT key simultaneously.

Check your computer operating manual for correct procedure.

To print a report, press the F10 function key. You will be

prompted for a Job Name, Address, City & State, and

Description. These are optional and they may contain any

data. The data entered at these prompts will be printed at

the top of the report*. Next, enter P to print to a printer,

or, D to print to disk. When you are ready to print the

report, press F10.

* This data will not print at top of Quick Reference Tables.

NOTE:

To print any of the Quick Reference Tables, press F10 while

viewing the table. The 'Print' input screen allows input of

job name, address and description, however, this information

will not be printed to any of the Quick Reference reports.

NOTE:

When printing reports or Quick Reference Tables that are

longer than one page, the program does NOT check for page

breaks. On a non-laser printer, you can set your printer to

'Skip Perforation'. This will leave a margin at the bottom of

each page, and continue at the top of the next page. Check

your printer's documentation for proper procedure. Laser

printers will automatically apply page breaks.

Page 22

-------------------------------------------------------------

QUICK REFERENCE TABLES

Equipment Ground Conductors

To determine the required size equipment ground conductor, as

per NEC Table 250-95.

Grounding Electrode Conductors

To determine the proper grounding electrode conductor size,

as  per NEC Table 250-94.

Kw To Amperes

To quickly convert single and three phase KW values to ampere

values and vice versa. Pressing PG UP & PG DN scrolls between

the single phase and three phase tables.

Underground Cover Requirements

To determine the minimum cover requirements of conduit,

underground cable, and other raceways, per NEC Table 300-5.

Metal Device Boxes

Table of metal device boxes and their cubic inch capacities.

Standard Pull & Junction Boxes

Table of standard pull & junction boxes and their cubic inch

capacities.

Standard Fuses & Breakers

Table of standard ratings of overcurrent devices.

Transformer Kva To Amperes

To quickly convert single and three phase transformer Kva

values to ampere values and vice versa. Pressing PG UP & PG

DN scrolls between the single phase and three phase tables.

NOTE:

The data for this table is located in the ELECTRC.DAT file,

and is read in by the program. This file must be located in

the same drive\directory as the main program file,

ELECTRC.EXE.

Page 23

-------------------------------------------------------------

Terminal/Conductor Temperature Limitations

The requrements of NEC Section 110-14(c).

Conductor Ampacity

Allowable ampacities and ambient temperature derating factors

of NEC Table 310-16. Pressing PG UP & PG DN scrolls the

table. NOTE: The data for this table is located in the

ELECTRC.DAT file, and is read in by the program. This file

must be located in the same drive\directory as the main

program file, ELECTRC.EXE.

SHORT CIRCUIT CALCULATIONS - Point To Point Method

The point to point method is a method of calculating

available fault currents.

To calculate the available fault current at various points

throughout an electrical distribution system. You can start

with the available short circuit current at a source point

(secondary of a utility transformer for example), and

determine the fault current available at any point beyond

that based on the voltage drop due to wire impedance and the

inductive effect of the circuit. Capacative reactance is

negligible at 600 volts or less, and is ignored. Note that

the values of effective impedance calculated by the program

are valid at 75 degrees C, and at 85 percent power factor of

the circuit. A maximum of ten points can be calculated,

single and three phase. Motor contribution is not presently

supportrd in this version of the software.

Method used to determine available short circuit current at

any point:

1. Obtain the available short circuit current at your

starting point:

If your starting point is the secondary of a utility

transformer, the utility company should be consulted

for this information. If your starting point is a

transformer and fault current is not known, determine

the fault current available at the secondary terminals

as follows:

A. Calculate the Multiplier:

Multiplier = 100 / Percent Transformer Impedance

Example:

277/480v, 3 phase 500 Kva transformer Percent

nameplate impedance = 2 percent

Multiplier = 100 / 2

Multiplier = 50

Page 24

-------------------------------------------------------------

B. Calculate short cct current at the secondary terminals:

Isca = Short circuit current at secondary terminals.

Isca = Transformer Full Load Amps x Multiplier

Example:

Isca = 500 amps x 50 'Multiplier from above'

Isca = 25000 amps

2. Calculate the C Factor:

C Factor = 1 / Wire Impedance Per Foot

Example:

500 kcmil copper conductor in steel conduit

From NEC Chapter 9, Table 9:

Impedance per 1000 feet = 0.050

Impedance per foot = 0.050 / 1000 = .00005

C Factor = 1 / .00005 = 20000

3. Calculate the F Factor:

L = One way conductor length from source point to the fault

I = available short circuit current at your starting point

C = C Factor

E = Line to line voltage at your starting point

NPC = Number of parallel conductors per phase

For 3 Phase Faults:

F Factor = (1.73 x L x I) / (NPC x C x E)

For 1 Phase Line to line faults:

F Factor = (2 x L x I) / (NPC x C x E)

Example:

277/480v, 3 phase source, I = 25000 amps,

150 feet #500 kcmil copper conductors, 1 per phase,

steel conduit, C = 20000

F Factor = (1.73 x 150 x 25000) / (1 x 20000 x 480)

F Factor = 6487500 / 9600000 = .6757813

4. Calculate the M Factor:

M Factor = 1 / (1 + F Factor)

Example:

M Factor = 1 / 1.6757813 = .5967366

5. Calculate available short circuit current at the fault:

Short Circuit Current At The Fault = Isca x M Factor

Isca = available short cct current at your starting point

Ifsca = Short circuit current at the fault

Example:

Ifsca = Isca x M Factor

Ifsca = 25000 x .5967366 = 14918 Amps

Page 25

-------------------------------------------------------------

Data Input And Calculation

The data input areas are where you will enter parameters for

the calculations. Use the UP ARROW and DOWN ARROW keys to

move from prompt to prompt. Using the ENTER key moves you

down through the prompts. Pressing the ESCAPE key aborts the

calculation and returns you to the main menu. An exception is

when you are selecting a choice from a group of options by

pressing one of the function keys. Pressing ESCAPE here only

backs you out of that selection area, without losing any data.

The first step in using the function is to input data at an

initialization area. Enter the number of points that you wish

to calculate fault currents for (maximum of 10).

Then press the PG DN key to access the data entry area for

point number 1 and proceed to enter data as follows:

Available Fault Current At Source - This will be the short

circuit amps available at the secondary of your utility or

distribution transformer, load side of main service

disconnect, etc, or wherever you choose to start the fault

calcs from. Note that if you are entering data for point

number 2, etc., The source would be the place where that

point is fed from.

One Way Conductor Length In Feet - The end to end length of

the wire run from the source to the location where the

available fault current will be calculated. Could be the

mains of the service equipment, line terminals of a

panelboard, etc. Use the one way length of one wire.

Number Of Parallel Conductors Per Phase - the number of

multiple conductors in parallel for each phase.

Conductor Size - The Awg or Kcmil size of the wire. If the

wire size is # 4/0, input 4/0 at the prompt. For 750 Kcmil,

input 750. Acceptable wire range is from #12 to 1000 Kcmil.

Line To Line Volts Of This Point -  The voltage available at

the location where the fault current will be calculated. 600

maximum. Do not include any voltage drop in this value.

Single Or Three Phase -  Phase of this point.

Description - Optional field for whatever you wish to enter.

F2 - Press the F2 function key to select the wire material

(copper or aluminum) and raceway type (steel, aluminum, pvc)

used to supply this point. Note that raceway type also

applies to cable armor. Also, the calculations are based on

three circuit conductors in the raceway. If the circuit

conductors for the point being calculated are contained

within a raceway where other circuit conductors are present,

the accuracy of the calculation could not be assured.

Page 26

-------------------------------------------------------------

Once all the above data has been entered, the results are

automatically calculated and the fault current amps is

displayed.

Pressing the F3 function key will show the details of the

calculation. The source current, the C Factor, F Factor, M

Factor, and the calculated fault current are displayed.

Pressing any key from the detail screen will return you to

the data entry area with all previously entered data intact.

Note that if you have not completely entered all required

data for at least one point, the F3 key will not work. Note

that the Description field need not be used, and leaving it

blank will not have any effect.

You can press PG UP or PG DN to scroll through the data entry

areas for each of the number of points that you inputted into

the initialization area. You can also PG UP until you are

back in the initialization area, change the number of points

to calculate, and PG DN through the areas without losing

data. However, if you change to a lesser number of points,

you will lose the data for the number of points greater than

the newly selected number of points.

A printout is available by pressing F10. See the

documentation for printing for details.

VOLTAGE DROP CALCULATOR

Calculates the voltage drop on existing or proposed single or

three phase resistive AC circuits (100% power factor). Copper

and aluminum conductors from #14 to 2000 Kcmil are supported.

Data Input:

Single or Three Phase is obvious.

Length Of Run is the length in feet of one conductor from the

source of power to the load terminals.

Source Voltage is the voltage measured at the source.

Amperage Of Load is the current required by the load. For

example, if the load is a resistance heater requiring 10 amps

to operate as designed, then the AMPERAGE would be entered as

10.

Wire Size is in the range of #18 Awg to 2000 Kcmil. Do not

include the # sign or the letters Awg or Kcmil. Enter the

numeric size of the wire (ex. 14, 1/0, 250, 750).

Copper or Aluminum prompt is self explanatory.

Page 27

-------------------------------------------------------------

After entering the above values, the program will calculate

and display:

1. The VOLTAGE DROP of the circuit (the number of volts

dropped).

2. The VOLTS AT LOAD (the voltage delivered to the load

terminals)

3. The % DROP (the percentage of the source voltage dropped)

Page 28

-------------------------------------------------------------

OTHER ELECTRICAL SOFTWARE AVAILABLE

-----------------------------------

LOADCALC Copyright 1991-96 By Robert J. La Capra

Version 2

LOADCALC performs service/feeder load calculations for single

dwelling units:

*      Standard Calculation Method (NEC Article 220).

*      Optional Calculation Method (NEC Article 220-30)

*      Additional Loads in Existing Dwelling Units

Calculation Method (NEC Article 220-31).

*      Calculates net computed load in VA and amperes,

determines minimum service entrance or feeder size.

CONTEXT SENSITIVE HELP:

*  Describes the expected input.

*  Provides special definitions or requirements &

refers to appropriate NEC Article/Section.

QUICK REFERENCE TABLES:

*  Grounding Electrode Conductor Sizes (NEC Tbl 250-94).

*  Service/Feeder Conductor Sizes (NEC 310, Note 3).

STANDARD CALCULATION METHOD:

*  Demand Factoring:

*  General Lighting, Small Appliance and Laundry Loads.

*  Cooktop, Range, Wall Oven.

*  Fixed Appliances.

*  Largest Motor Load.

*  Additional User-Definable Loads:

*  2 additional appliance loads, motor/nonmotor,

fixed/nonfixed.

*  1 additional lighting

load,continuous/noncontinuous.

*  Automatic selection of the larger of heating

or cooling loads.

OPTIONAL CALCULATION METHOD:

*  Demand factoring of 'other loads' as per NEC 220-30.

*  Allows input of heating system type as per NEC Table

220-30, automatically determines the larger of heating

or cooling load.

*  Additional User-Definable Loads:

2 additional appliance loads, 1 additional

lighting load.

ADDITIONAL LOADS IN EXISTING DWELLING UNITS:

*  Load calculations for existing dwelling units

presently served by a 120/240 volt or 120/208Y

service.

Page 29

-------------------------------------------------------------

PRINTED REPORTS:

*  Professional, detailed reports for all program

functions.

*  Send reports out to a printer, or to an ASCII disk

file (where you can then import the report into

your word processor and fine tune the appearance

before printing).

*  Input up to four lines of data which will print at

the top of your report.

*  Printer output is generic, will work on any printer

connected to parallel port 1 or 2.

*  User selectable Formfeed option.

'WHAT-IF'  DATA INPUT:

*  Quickly and easily see what effect a change of one

data item will have on the result of the design

currently in progress.

*  Once all data has been entered within a function

and the function has calculated the result,

individual data items can be changed, one at a

time, and the function will automatically

recalculate the results instantly.

*  Great for quick comparisons of alternate design specs.

NEC COMPLIANCE:

LOADCALC has been written to produce design specifications

that comply with the 1996 National Electrical Code

requirements.

SYSTEM REQUIREMENTS:

LOADCALC is not a WINDOWS program, but it will run under

WINDOWS. To run LOADCALC, you will need to have the

following minimum hardware configuration:

*    An IBM or compatible computer.

*    Any brand or version of DOS,  2.11 or greater.

*    200 K of free memory available.

*    One floppy disk drive.

*    Monochrome or color monitor.

Page 30

-------------------------------------------------------------

Sample Printed Report From LOADCALC Version 2

STANDARD SERVICE/FEEDER LOAD CALCULATION - One Family Dwelling

Ralph Colbert

23 Maple Tree Lane

Byram Twsp., NJ 18539

Block 55, Lot 10

�������������������������������������������������������������

General Lighting ... : 3200 Sq. Feet x    3 VA =  9600 VA

Small Appliance .... :    2 Circuits x 1500 VA =  3000 VA

Laundry ............ :    1 Circuits x 1500 VA =  1500 VA

---------------------------------------------------------

Total General Light & Small Appliance ........ : 14100 VA

The First   3000 VA @ 100%  =   3000 VA

Remaining  11100 VA @  35%  =   3885 VA

---------------------------------------

GENERAL LIGHTING, SMALL APPLIANCE & LAUNDRY DEMAND LOAD:  6885 VA

Heating Demand ..... : 20000 VA @ 100% = 20000 VA

Cooling Demand ..... :  9000 VA @ 100% =  9000 VA

LARGER OF HEATING OR COOLING DEMAND LOADS (Heating) .. : 20000 VA

Cooktop ................. :  4000 VA

Range ................... : 12000 VA

Wall Oven ............... :  5000 VA

COOKING EQUIPMENT DEMAND LOAD ........................ : 13850 VA

Dryer ................... :  5000 VA

DRYER DEMAND LOAD .................................... :  5000 VA

Water Heater ............ :  6000 VA

Attic Fan ............... :  1000 VA

Compactor ............... :   800 VA

Dishwasher .............. :  1200 VA

Disposal ................ :   650 VA

Well Pump ............... :  1100 VA

------------------------------------

Fixed Appliance Total ... : 10750 VA

10750 VA @  75% Demand:  8063 VA

FIXED APPLIANCE DEMAND LOAD .......................... :  8063 VA

Largest Motor: Well Pump ............... : @ 1100 VA

25% OF LARGEST MOTOR LOAD ............................ :   275 VA

______________________________________________________________

NET COMPUTED LOAD ............................. : 54073 VA

120/240 VOLT SERVICE/FEEDER LOAD .............. : 225 AMPERES